Painting Water Storage Tanks- Inspection—12-15-10

Painting Inspection is a specialized field that is usually assigned to an outside consultant. The following areas represent critical items that must be monitored.

- Pre- construction review

- Check specifications for surface preparation

- Check paint system

- Determine the work that will be measured (An example is welding repair. If there are a lot of repairs based on the pre design inspection, it will have a per inch unit cost. If it is minimal, it will considered incidental work)

- Taking the Tank out of Service

- Coordinate with Operations

- Remember entering an empty tank is a confined entry procedure

- Verify that the electric service is locked out

- Verify that fill valves are closed and in manual mode

- Verify that the tank is clean unless cleaning is part of the contractor’s work

- Surface preparation

- Monitor for paint chips leaving the site

- Observe the surface condition for compliance

- Surface preparation with lead paint

- Review the lead paint test results

- Obtain additional samples to verify lead hazard level

- Check containment provisions to keep lead based paint from leaving the site

- Obtain copies of the hazardous waste manifest to verify proper disposal

- Coating application

- Verify that the product on site matches the specification

- Verify that the application method is suitable for the product on site

- Measure the air temperature, humidity, and surface temperature for compliance with the application specifications and product recommendations

- Monitor the product application and record the approximate area and location applied per session

- Check the dry film thickness

- Verify drying time between coats

- Monitor the next coats as above

- Conduct spark tests and mark failures

- Recheck failures

- Prepare for disinfection

- Verify that all cathodic protection equipment is installed inside the tank

- Check tank for tools and/or other items that do not belong in the tank and remove

- Close all access ports

- Fill tank according to the disinfection procedure

- Pull bacti samples

- Check bacti results for proper disinfection

- Inform Operations that the tank is ready to be put in service if bacti tests pass.